


June 22, 2000

Revised 8/24/00

Subject:
PM5 PRESSURE VESSEL AND SRV INFORMATION

From:
T. Snape

To:

J. Sutherland

Cc:

D. Sanborn
D. Nason
D. Cook
C. Stewart

The following information was gathered during the 6/22/00 planned maintenance outage:

Tending Side Dryer Head Information:

If a U-1 nameplate is present, the National Board Number is included.

If no National Board Number is listed, then no nameplate could be found.

Note that nameplates are mostly obscured by grime.  Dryer drive side heads are also very dirty and very difficult to access due to machine frame and drive gears.  No nameplates were visible on any drive side dry head, though it was impossible to do a thorough survey due to the conditions.

EQ. ID
Tending Side Head Information:

E50DY01
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY02
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY03
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY04
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY05
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY06
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY07
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY08
RICE BARTON CORPORATION WORCESTER MASS 1941

E50DY09
RICE BARTON CORPORATION WORCESTER MASS 1947

E50DY10 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1892

E50DY11 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1892

E50DY12 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1906

E50DY13
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1892

E50DY14 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1892

E50DY15 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1892

E50DY16 
RICE BARTON CORPORATION WORCESTER MASS 1946

E50DY17 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1916

E50DY18 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1909

E50DY19 
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1892

E50DY20
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1906

E50DY21
RICE BARTON CORPORATION WORCESTER MASS 1952

E50DY22
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1906

E50DY23 
SANDY HILL 1975 
NAMEPLATE NB# 1481

E50DY24
J.H.HORNE & SONS CO. LAWRENCE MASS

E50DY25
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1906

E50DY26
RICE, BARTON & FALES MACHINE & IRON CO. MAKERS. WORCESTER MASS 1906

E50DY27
SANDY HILL 6146  1973  
NAMEPLATE NB# 1284

E50DY28
BELOIT IRON WORKS BELOIT WIS

E50DY29
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4924

E50DY30
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4922

E50DY31
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4923

E50DY32
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4917

E50DY33
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4915

E50DY34
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4914

E50DY35
TAMPELLA SANDY HILL 1992 
NAMEPLATE NB# 4918(? Last digit not clear)

Pressure Vessel U-1 Nameplate Information:

LN Flash Condensate Tank (Equipment ID ?)  –



N3868


LINCOLN PULP & PAPER CO


LINCOLN-MAINE


SIZE 30”X60”
ITEM S-2


TP 187.5
WP 125


DATE 1974
NO. 9804-119


CUSTOMER P.O. NO. 11211 


MASONELILAN INTERNATIONAL INC


NORWOOD MASSACHUSETTS USA

Vacuum Receiver Tank  (Equipment ID ?) -


MASS ENGINEERING CO. INC.


SHOP O.N.  N-3870


MECO NO. T.P. 250 P.S.I.G.


NAT’L BD. NO. 2292


MAX W.P. 125 P.S.I.G.


MAX TEMP 650 F


YEAR 1974



SH/HD THK 1/4” – 5/16”


Condenser E50D20 –



NAT’L BD 8178



CERTIFIED BY KETEMA INC. HEAT TRANSFER DIV



SHELL SIDE 150 MAX WP AT 300 F



TUBE SIDE 150 MAX WP AT 300 F



SHELL MDMT –20 F AT 150 PSI



TUBE MDMT –20 F AT 150 PSI



MANUFACTURERS SERIAL NO. U942355A



YEAR BUILT 1994



TYPE 1-VW-2(AJM) SIZE 13-A-120


Short Nest Bottom Separator E50SP04 –



NATL BOARD NO. 12262



BUCKEYE FABRICATING CO. INC



DAYTON OHIO



MAX WP 150



MAX TEMP 650 F



SHELL ¼



HEAD ¼ RAD 18



YEAR BUILT 1977


Short Nest Top Separator E50SP05 –



NATL BOARD NO. 12261



BUCKEYE FABRICATING CO. INC



DAYTON OHIO



MAX WP 150



MAX TEMP 650 F



SHELL ¼



HEAD ¼ RAD 18



YEAR BUILT 1977


Safety Relief Valve Nameplate Information:


PM5 Turbine Exhaust SRV 45



Manufacturers Nameplate:




CONSOLIDATED SAFETY VALVE




SIZE 6 
TYPE 1511QS20






SET 47 PSI
SER BW02273




BD     2 PSI
SEAT DIA 3.750




CAP  32613 LBS.ST./HR. AT SAT




F.D. RIGGIO 
LIFT .936 IN



Repair Tag:




REPAIRED BY SEELY & JONES INC




DATE 11-98




SET 58

REPAIR SN Q-1689




CAP 13954 LB/HR


PM5 Long Nest Steam Header SRV 47:



Manufacturers Nameplate:




CONSOLIDATED




SIZE 8
TYPE 1905T7P1-1




SER NO.  TD 41406




SET 45

MATL STEEL



Repair Tag:




REPAIRED BY SEVCO




SET 50

CAP 87836




DATE 12-95




NATIONAL BOARD REPAIR SYMBOL STAMP NO. 150




101233



Also carries a Sevco Survey Tag with no. 05-00010


PM5 Short Nest Steam Header:



Manufacturers Nameplate:




CONSOLIDATED




SEVCO INC




SIZE 2 
TYPE 1511K20




SER NO BY23512




SET 75

LIFT .383




CAP 7638    LB/HR AT SAT




B/M 92185
DATE 8/17/92



Repair Tag:




REPAIRED BY SEVCO




SET 145
CAP 13628




DATE 12/92




NATIONAL BOARD REPAIR SYMBOL STAMP NO. 150




SO 2025


