Munroe Vertical Clarifier; Complete with L-Shaped Access Platform

Model VC-300 | 105 GPM

Condition; Good

Location:

Brainerd, MN 56401 USA

| Design Criteria |  |
| --- | --- |
| Design Flow Rate | 105 GPM |
| Monroe Model | VC-300 |
| Approximate Clarifier Dimensions with Pretreatment Tanks | 6'-0" W x 15'-0" L x 14'-0" H |
| Effective Settling Area | 300 ft2 |
| Actual Settling Area | 524 ft2 |
| Tank Material of Construction | 304 Stainless Steel |
| Structure Material of Construction | 304 Stainless Steel |
| Separator Plate Construction | 304 Stainless Steel |
| Stainless Steel Finish | All Welds to be Passivated |
| Sludge Removal | Pyramid Hopper |
| Fastener Material | 18-8 Stainless Steel (A325 Mech. Galvanized for Structural) |

| Components & Features |  |
| --- | --- |
| Flash Mix Tank | - (1) 6" flanged influent connection - 150-gallon capacity - Constant speed flash mixer with 316L SS shaft and impellers - Up to ½ HP inverter duty TEFC motor (3/60/460V) |
| Flocculation Tank | - Mounted integrally to flash mix tank - 450-gallon capacity - Flocculation mechanism with 316L SS shaft and impeller - Up to ¾ HP inverter duty TEFC motor with loose VFD (3/60/460V) |
| Influent Area | - Flanged influent connection - Feed channels for separation plates - Diffusion walls with slotted inlet orifices for flow distribution |
| Separation Section | - Provides required effective separation area at design flow - Separation plates are sloped 55° from horizontal - 2" spacing between each plate - Structural rear wall contributes to the effective settling area |
| Pyramid Sludge Hopper | - (1) pyramid sludge hopper - (1) 4" flanged connection for purging per hopper (purging equipment by others) - Included blind flange with blow out nozzle on sludge discharge piping - Two (2) ½" sludge sampling ports - Hinged access port provided for ease of access |
| Effluent Chamber | - Hinged 304 stainless steel effluent launder with flow controlling orifices - One (1) 6" flanged effluent connection |
| Access Platform | - (1) “L” shaped access platform to run the length of the clarifier and along the effluent - Platform and supports to be coated carbon steel - Platform to be supported by clarifier - Includes (1) aluminum ladder with safety gate - Aluminum bar grating - Aluminum handrails with fittings - Conforms to OSHA standards |